## Datapoint_modified_RBC_05102023
Variable | Data Point Name | Description | Dymola Model Output Variable Expressions | Unit
var1 | Ease Zone: Room Temperature | East Zone Room Temperature | flo.temAirEas.T | K
var2 | Ease Zone: Room Cooling Setpoint | East Zone Room Cooling Setpoint | conVAVEas.TZonCooSet | K
var3 | Ease Zone: Room Heating Setpoint | East Zone Room Heating Setpoint | conVAVEas.TZonHeaSet | K
var4 | Ease Zone: Electric Reheating Coil Power Control Signal | East Zone Reheating Coil Valve Power Control Signal | conVAVEas.yVal | --
var5 | Ease Zone: Electric Reheating Coil Power Consumption | East Zone Reheating Coil Valve Power Consumption | eas.terHea.Q2_flow | W
var6 | Ease Zone: VAV Discharge Air Temperature | East Zone VAV discharge air temperature | TSupEas.T | K
var8 | Ease Zone: VAV Damper Position | East Zone VAV Damper Position | eas.y_actual | --
var9 | Ease Zone: VAV Damper Control Signal (Pressure independent) | East Zone VAV Damper Control Signal (demand) | conVAVEas.yDam | --
var11 | Ease Zone: VAV Discharge Air Flow Rate | East Zone VAV Discharge Air Flow Rate | VSupEas_flow.V_flow | m3/s
var12 | South Zone: Room Temperature | South Zone Room Temperature | flo.temAirSou.T | K
var13 | South Zone: Room Cooling Setpoint | South Zone Room Cooling Setpoint | conVAVSou.TZonCooSet | K
var14 | South Zone: Room Heating Setpoint | South Zone Room Heating Setpoint | conVAVSou.TZonHeaSet | K
var15 | South Zone: Electric Reheating Coil Power Control Signal | South Zone Reheating Coil Valve Power Control Signal | conVAVSou.yVal | --
var16 | South Zone: Electric Reheating Coil Power Consumption | South Zone Reheating Coil Valve Power Consumption | sou.terHea.Q2_flow | W
var17 | South Zone: VAV Discharge Air Temperature | South Zone VAV discharge air temperature | TSupSou.T | K
var19 | South Zone: VAV Damper Position | South Zone VAV Damper Position | sou.y_actual | --
var20 | South Zone: VAV Damper Control Signal (Pressure independent) | South Zone VAV Damper Control Signal (demand) | conVAVSou.yDam | --
var22 | South Zone: VAV Discharge Air Flow Rate | South Zone VAV Discharge Air Flow Rate | VSupSou_flow.V_flow | m3/s
var23 | West Zone: Room Temperature | West Zone Room Temperature | flo.temAirWes.T | K
var24 | West Zone: Room Cooling Setpoint | West Zone Room Cooling Setpoint | conVAVWes.TZonCooSet | K
var25 | West Zone: Room Heating Setpoint | West Zone Room Heating Setpoint | conVAVWes.TZonHeaSet | K
var26 | West Zone: Electric Reheating Coil Power Control Signal | West Zone Reheating Coil Valve Power Control Signal | conVAVWes.yVal | --
var27 | West Zone: Electric Reheating Coil Power Consumption | West Zone Reheating Coil Valve Power Consumption | wes.terHea.Q2_flow | W
var28 | West Zone: VAV Discharge Air Temperature | West Zone VAV discharge air temperature | TSupWes.T | K
var30 | West Zone: VAV Damper Position | West Zone VAV Damper Position | wes.y_actual | --
var31 | West Zone: VAV Damper Control Signal (Pressure independent) | West Zone VAV Damper Control Signal (demand) | conVAVWes.yDam | --
var33 | West Zone: VAV Discharge Air Flow Rate | West Zone VAV Discharge Air Flow Rate | VSupWes_flow.V_flow | m3/s
var34 | North Zone: Room Temperature | North Zone Room Temperature | flo.temAirNor.T | K
var35 | North Zone: Room Cooling Setpoint | North Zone Room Cooling Setpoint | conVAVNor.TZonCooSet | K
var36 | North Zone: Room Heating Setpoint | North Zone Room Heating Setpoint | conVAVNor.TZonHeaSet | K
var37 | North Zone: Electric Reheating Coil Power Control Signal | North Zone Reheating Coil Valve Power Control Signal | conVAVNor.yVal | --
var38 | North Zone: Electric Reheating Coil Power Consumption | North Zone Reheating Coil Valve Power Consumption | nor.terHea.Q2_flow | W
var39 | North Zone: VAV Discharge Air Temperature | North Zone VAV discharge air temperature | TSupNor.T | K
var41 | North Zone: VAV Damper Position | North Zone VAV Damper Position | nor.y_actual | --
var42 | North Zone: VAV Damper Control Signal (Pressure independent) | North Zone VAV Damper Control Signal (demand) | conVAVNor.yDam | --
var44 | North Zone: VAV Discharge Air Flow Rate | North Zone VAV Discharge Air Flow Rate | VSupNor_flow.V_flow | m3/s
var45 | Core Zone: Room Temperature | Core Zone Room Temperature | flo.temAirPer5.T | K
var46 | Core Zone: Room Cooling Setpoint | Core Zone Room Cooling Setpoint | conVAVCor.TZonCooSet | K
var47 | Core Zone: Room Heating Setpoint | Core Zone Room Heating Setpoint | conVAVCor.TZonHeaSet | K
var48 | Core Zone: Electric Reheating Coil Power Control Signal | Core Zone Reheating Coil Valve Power Control Signal | conVAVCor.yVal | --
var49 | Core Zone: Electric Reheating Coil Power Consumption | Core Zone Reheating Coil Valve Power Consumption | cor.terHea.Q2_flow | W
var50 | Core Zone: VAV Discharge Air Temperature | Core Zone VAV discharge air temperature | TSupCor.T | K
var52 | Core Zone: VAV Damper Position | Core Zone VAV Damper Position | cor.y_actual | --
var53 | Core Zone: VAV Damper Control Signal (Pressure independent) | Core Zone VAV Damper Control Signal (demand) | conVAVCor.yDam | --
var55 | Core Zone: VAV Discharge Air Flow Rate | Core Zone VAV Discharge Air Flow Rate | VSupCor_flow.V_flow | m3/s
var56 | AHU: Supply Air Temperature | AHU supply air temperature | TSup.T | K
var57 | AHU: Supply Air Temperature Set Point | AHU supply air temperature set point | conAHU.TSupSet | K
var58 | AHU: Outdoor Air Dry Bulb Temperature | AHU outdoor air dry bulb temperature | TOut.y | K
var59 | AHU: Outdoor Air Wet Bulb Temperature | AHU outdoor air wet bulb temperature | weaDat.weaBus.TWetBul | K
var60 | AHU: Mixed Air Temperature | AHU mixed air temperature | TMix.T | K
var61 | AHU: Return Air Temperature | AHU return air temperature | TRet.T | K
var62 | AHU: Cooling Coil Discharge Air Temperature | Cooling coil discharge air temperature | cooCoi.T2[1] | K
var63 | AHU: Supply Air Fan Status | AHU supply air fan status; 0-off, 1-on | conAHU.ySupFan | --
var64 | AHU: Supply Air Fan Speed Control Signal | AHU supply air fan speed; ranges from 0 to 1; 0 - fan speed is 0%, 1 - fan speed is 100% | fanSup.y | --
var65 | AHU: Outdoor Air Damper Control Signal (Screen Value) | Control signal for AHU outdoor air damper from BAS; ranges from 0 to 1; 0 – damper should be fully closed, 1 – damper should be fully open | eco.yOut | --
var66 | AHU: Outdoor Air Damper Stuck Position (True Value) | True value for AHU outdoor air damper stuck position | eco.damOut.y_actual | --
var67 | AHU: Return Air Damper Control Signal | Control signal for AHU return air damper; ranges from 0 to 1; 0 – damper should be fully closed, 1 – damper should be fully open | eco.yRet | --
var68 | AHU: Exhaust Air Damper Control Signal | Control signal for AHU exhaust air damper; ranges from 0 to 1; 0 – damper should be fully closed, 1 – damper should be fully open | eco.yExh | --
var69 | AHU: Supply Air Mass Flow Rate | Supply air mass flow rate | eco.port_Sup.m_flow | kg/s
var70 | AHU: Outdoor Air Mass Flow Rate | Outdoor air mass flow rate | eco.port_Out.m_flow | kg/s
var71 | AHU: Return Air Mass Flow Rate | Return air mass flow rate in the mixing box | eco.damRet.port_a.m_flow | kg/s
var72 | AHU: Exhaust Air Mass Flow Rate | Exhaust air mass flow rate in the mixing box | eco.damExh.port_a.m_flow | kg/s
var73 | AHU: Cooling Coil Valve Control Signal (Screen Value) | Control signal for AHU cooling coil valve from BAS; ranges from 0 to 1; 0 – valve should be fully closed, 1 – valve should be fully open | watVal.y | --
var74 | AHU: Cooling Coil Valve Stuck Position (True Value) | True value for for AHU cooling coil valve stuck position | watVal.y_actual | --
var75 | AHU: Heating Coil Valve Control Signal | Control signal for AHU heating coil valve; ranges from 0 to 1; 0 – valve should be fully closed, 1 – valve should be fully open | HWVal.y | --
var76 | AHU: Supply Air Duct Static Pressure | Measured AHU supply air duct static pressure | dpDisSupFan.p_rel | Pa
var77 | AHU: Supply Air Duct Static Pressure Set Point | AHU supply air duct static pressure setpoint | conAHU.supFan.staPreSetRes.y | Pa
var78 | AHU: Cooling coil heat transfer rate | Cooling coil heat transfer rate | cooCoi.Q1_flow | W
var79 | AHU: Heating coil heat transfer rate | Heating coil heat transfer rate | heaCoi.Q1_flow | W
var80 | AHU: Supply air fan power consumption | Power consumption of a supply air fan | fanSup.P | W
var82 | System: Occupancy Mode Indicator | Indicator if the system operates in occupied mode; 1- occupied mode, 0-unoccupied mode | occSch.occupied | --
var83 | Chilled Water Loop: Supply Chilled Water Temperature | Temperature of the water leaving the chilled water loop | TCHWSup.T | K
var84 | Chilled Water Loop: Return Chilled Water Temperature | Temperature of the water entering the chilled water loop | TCHWRet.T | K
var85 | Condenser Water Loop: Supply Cooling Water Temperature | Temperature of the water leaving the condenser water loop | TCWSup.T | K
var86 | Condenser Water Loop: Return Cooling Water Temperature | Temperature of the water entering the condenser water loop | TCWRet.T | K
var87 | Hot Water Loop: Supply HotWater Temperature | Temperature of the water leaving the hot water loop | THWSup.T | K
var88 | Hot Water Loop: Return Hot Water Temperature | Temperature of the water entering the hot water loop | THWRet.T | K
var89 | Chilled Water Loop: Supply Chilled Water Temperature Set Point | Set point of temperature of the water leaving the chilled water loop | temDifPreRes.TSet | K
var90 | Chilled Water Loop: Differential Pressure | Measured differential pressure of the chilled water loop | senRelPre.p_rel | Pa
var91 | Chilled Water Loop: Differential Pressure Setpoint | Differential pressure setpoint of the chilled water loop | temDifPreRes.dpSet | Pa
var92 | Hot Water Loop: Supply Hot Water Temperature Set Point | Set point of temperature of the hot water leaving a boiler | triResHW.TSet | K
var93 | Hot Water Loop: Differential Pressure | Measured differential pressure setpoint of the hot water loop | senRelPreHW.p_rel | Pa
var94 | Hot Water Loop: Differential Pressure Setpoint | Differential pressure setpoint of the hot water loop | triResHW.dpSet | Pa
var95 | Chiller: On off Signal | Chiller on off Signal | chiOn.y | --
var96 | WSE: On off Signal | WSE on off Signal | wseOn.y | --
var97 | Boiler: Control Signal | Boiler Control Signal | boi.y | --
var98 | Chiller: Bypass Valve Control Signal | Chiller bypass valve control signal (0 - when free cooling mode is deactivated; 1 - when free cooling is activated) | chiWSE.val6.y | --
var99 | WSE: Bypass Valve Control Signal | WSEbypass valve control signal (0 - when fully mechanic cooling is activated; 1 - when fully mechanic cooling is activated) | chiWSE.val5.y | --
var100 | Cooling Tower: Cooling Tower Fan Speed Control Signal | Cooling tower fan speed control signal | cooTow.y | --
var101 | Condenser Water Loop: Shutoff Valve Control Signal | Condenser Water Loop Shutoff Valve Control Signal: 0 - closed; 1- open | val.y | --
var102 | Hot Water Loop: Boiler Shutoff Valve Control Signal | Hot Water Loop Boiler Shutoff Valve Control Signal: 0 - closed; 1- open | boiIsoVal.y | --
var103 | Hot Water Loop: Bypass Valve Control Signal | Hot Water Loop Bypass Valve Control Signal: 0-1 | valBypBoi.y | --
var104 | Chilled Water Loop: Chilled Water Flow Rate into the Cooling Coil | Chilled water flow rate of the chilled water loop into the cooling coil | cooCoi.port_a1.m_flow | kg/s
var105 | Chiller: Chilled Water Flow Rate | Chilled water flow rate of the chiller | chiWSE.chiPar.port_a2.m_flow | kg/s
var106 | WSE: Chilled Water Flow Rate | Chilled water flow rate of the WSE | chiWSE.wse.port_a2.m_flow | kg/s
var107 | Condenser Water Loop: Cooling Water Flow Rate | Flow rate of the condenser water loop | cooTow.port_a.m_flow | kg/s
var108 | Chiller: Cooling Water Flow Rate | Cooling water flow rate of the chiller | chiWSE.chiPar.port_a1.m_flow | kg/s
var109 | WSE: Cooling Water Flow Rate | Cooling water flow rate of the WSE | chiWSE.wse.port_a1.m_flow | kg/s
var110 | Hot Water Loop: Hot Water Flow Rate into the Heating Coil | Flow rate of the hot water loop into the heating coil | heaCoi.port_a1.m_flow | kg/s
var111 | Boiler: Boiler Hot Water Flow Rate | Flow rate of the hot water loop into the boiler | boi.port_a.m_flow | kg/s
var112 | Hot Water Loop: Bypass Hot Water Flow Rate | Flow rate of the hot water loop in the bypass | valBypBoi.port_a.m_flow | kg/s
var113 | Chiller: Power consumption | Power consumption of a chiller | chiWSE.chiPar.chi[1].P | W
var114 | Boiler: Gas consumption | Gas consumption (mass flow rate) of a boiler | boi.mFue_flow | kg/s
var115 | Chilled Water Pump: Power consumption | Power consumption of the chilled water pump | chiWSE.pum.P[1] | W
var116 | Cooling Water Pump: Power consumption | Power consumption of the cooling water pump | pumCW.P | W
var117 | Hot Water Pump: Power consumption | Power consumption of the hot water pump | pumHW.P | W
var118 | Cooling Tower: Fan Power consumption | Power consumption of the cooling tower fan | cooTow.PFan | W
var119 | Chilled Water Pump: Speed Control Signal | Speed Control Signal of the chilled water pump | chiWSE.yPum[1] | --
var120 | Cooling Water Pump: Speed Control Signal | Speed Control Signal of the cooling water pump | pumCW.y | --
var121 | Hot Water Pump: Speed Control Signal | Speed Control Signal of the hot water pump | pumHW.y_actual | --
var122 | System: Cooling Mode Control Signal | Cooling Mode Control Signal: Free cooling - 1, Partial Mechanical - 2, Full Mechanical - 3, Off - 4 | cooModCon.y | --
var123 | System: Chiller Plant Equipment Operation Signal | Chiller Plant Equipment Operation Signal: 0 - off; 1 - on | chiPlaEnaDis.yPla | --
var124 | System: Boiler Plant Equipment Operation Signal | Boiler Plant Equipment Operation Signal: 0 - off; 1 - on | boiPlaEnaDis.yPla | --
var126 | AHU: Return Air Damper Actual Position (True Value) | True value for AHU return air damper position | eco.damRet.y_actual | --
var127 | AHU: Exhaust Air Damper Actual Position (True Value) | True value for AHU exhaust air damper position | eco.damExh.y_actual | --