## CoolingSeason
Index | scenarios |  | faultparameters
0 | BaselineSystem |  | -
1 | TCHWSup_p1 | Chilled water supply temperature sensor positive bias - 1 K | {'faultTCHWSup.active':True} {'TCHWSup.bias.k':1}
2 | TCHWSup_m1 | Chilled water supply temperature sensor negative bias - 1 K | {'faultTCHWSup.active':True} {'TCHWSup.bias.k':-1}
3 | TCHWSup_p2 | Chilled water supply temperature sensor positive bias - 2 K | {'faultTCHWSup.active':True} {'TCHWSup.bias.k':2}
4 | TCHWSup_m2 | Chilled water supply temperature sensor negative bias - 2K | {'faultTCHWSup.active':True} {'TCHWSup.bias.k':-2}
5 | TCWSup_p1 | Cooling water supply temperature sensor positive bias - 1 K | {'faultTCWSup.active':True} {'TCWSup.bias.k':1}
6 | TCWSup_m1 | Cooling water supply temperature sensor negative bias - 1 K | {'faultTCWSup.active':True} {'TCWSup.bias.k':-1}
7 | TCWSup_p2 | Cooling water supply temperature sensor positive bias - 2 K | {'faultTCWSup.active':True} {'TCWSup.bias.k':2}
8 | TCWSup_m2 | Cooling water supply temperature sensor negative bias - 2K | {'faultTCWSup.active':True} {'TCWSup.bias.k':-2}
9 | RelPreCHW_p5000 | Chilled water differential pressure sensor positive bias - 5000 Pa | {'faultRelPre.active':True} {'senRelPre.bias.k':5000}
10 | RelPreCHW_m5000 | Chilled water differential pressure sensor negative bias - 5000 Pa | {'faultRelPre.active':True} {'senRelPre.bias.k':-5000}
11 | RelPreCHW_p10000 | Chilled water differential pressure sensor positive bias - 10000 Pa | {'faultRelPre.active':True} {'senRelPre.bias.k':10000}
12 | RelPreCHW_m10000 | Chilled water differential pressure sensor negative bias - 10000 Pa | {'faultRelPre.active':True} {'senRelPre.bias.k':-10000}
13 | Vout_p15 | Outdoor air flow rate sensor positive scale error - 15% | {'faultVOut.active':True} {'VOut1.sca.k':1.15}
14 | Vout_m15 | Outdoor air flow rate sensor negative scale error - 15% | {'faultVOut.active':True} {'VOut1.sca.k':0.85}
15 | Vout_p30 | Outdoor air flow rate sensor positive scale error - 30% | {'faultVOut.active':True} {'VOut1.sca.k':1.3}
16 | Vout_m30 | Outdoor air flow rate sensor negative scale error - 30% | {'faultVOut.active':True} {'VOut1.sca.k':0.7}
17 | TSup_p1 | AHU supply air temperature sensor positive bias - 1 K | {'faultTSup.active':True} {'TSup.bias.k':1}
18 | TSup_m1 | AHU supply air temperature sensor negative bias - 1 K | {'faultTSup.active':True} {'TSup.bias.k':-1}
19 | TSup_p2 | AHU supply air temperature sensor positive bias - 2 K | {'faultTSup.active':True} {'TSup.bias.k':2}
20 | TSup_m2 | AHU supply air temperature sensor negative bias - 2K | {'faultTSup.active':True} {'TSup.bias.k':-2}
21 | TMix_p1 | Mix air temperature sensor positive bias - 1 K | {'faultTMix.active':True} {'TMix.bias.k':1}
22 | TMix_m1 | Mix air temperature sensor negative bias - 1 K | {'faultTMix.active':True} {'TMix.bias.k':-1}
23 | TMix_p2 | Mix air temperature sensor positive bias - 2 K | {'faultTMix.active':True} {'TMix.bias.k':2}
24 | TMix_m2 | Mix air temperature sensor negative bias - 2K | {'faultTMix.active':True} {'TMix.bias.k':-2}
25 | TRet_p1 | Return air temperature sensor positive bias - 1 K | {'faultTRet.active':True} {'TRet.bias.k':1}
26 | TRet_m1 | Return air temperature sensor negative bias - 1 K | {'faultTRet.active':True} {'TRet.bias.k':-1}
27 | TRet_p2 | Return air temperature sensor positive bias - 2 K | {'faultTRet.active':True} {'TRet.bias.k':2}
28 | TRet_m2 | Return air temperature sensor negative bias - 2K | {'faultTRet.active':True} {'TRet.bias.k':-2}
29 | RelPreAir_p15 | Air loop differential pressure sensor positive bias - 15 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':15}
30 | RelPreAir_m15 | Air loop differential pressure sensor negative bias - 15 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':-15}
31 | RelPreAir_p25 | Air loop differential pressure sensor positive bias - 25 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':25}
32 | RelPreAir_m25 | Air loop differential pressure sensor negative bias - 25 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':-25}
33 | TAirSou_p1 | South zone air temperature sensor positive bias - 1K | {'faulttemAirSou.active':True} {'flo.temAirSou.bias.k':1}
34 | TAirSou_m1 | South zone air temperature sensor negative bias - 1K | {'faulttemAirSou.active':True} {'flo.temAirSou.bias.k':-1}
35 | TAirSou_p2 | South zone air temperature sensor positive bias - 2K | {'faulttemAirSou.active':True} {'flo.temAirSou.bias.k':2}
36 | TAirSou_m2 | South zone air temperature sensor negative bias - 2K | {'faulttemAirSou.active':True} {'flo.temAirSou.bias.k':-2}
37 | TSupSou_p1 | South zone discharging air temperature sensor positive bias - 1K | {'faultTSupSou.active':True} {'TSupSou.bias.k':1}
38 | TSupSou_m1 | South zone discharging air temperature sensor negative bias - 1K | {'faultTSupSou.active':True} {'TSupSou.bias.k':-1}
39 | TSupSou_p2 | South zone discharging air temperature sensor positive bias - 2K | {'faultTSupSou.active':True} {'TSupSou.bias.k':2}
40 | TSupSou_m2 | South zone discharging air temperature sensor negative bias - 2K | {'faultTSupSou.active':True} {'TSupSou.bias.k':-2}
41 | VSupSou_flow_p15 | South zone air flow rate sensor positive scale error - 15% | {'faultVSupSou_flow.active':True} {'VSupSou_flow.sca.k':1.15}
42 | VSupSou_flow_m15 | South zone air flow rate sensor negative scale error - 15% | {'faultVSupSou_flow.active':True} {'VSupSou_flow.sca.k':0.85}
43 | VSupSou_flow_p30 | South zone air flow rate sensor positive scale error - 30% | {'faultVSupSou_flow.active':True} {'VSupSou_flow.sca.k':1.3}
44 | VSupSou_flow_m30 | South zone air flow rate sensor negative scale error - 30% | {'faultVSupSou_flow.active':True} {'VSupSou_flow.sca.k':0.7}
45 | SupDucLea_10 | Air loop supply duct leakage - FIR=10% | {'faultSupDucLea.active':True} {'leaFra.k':-0.12} | {'faultSupDucLea.active':True} {'leaFra.k':-0.1*1.2}
46 | SupDucLea_20 | Air loop supply duct leakage - FIR=20% | {'faultSupDucLea.active':True} {'leaFra.k':-0.24} | {'faultSupDucLea.active':True} {'leaFra.k':-0.2*1.2}
47 | AirDucFou_10 | Air loop duct fouling - FIR=10% | {'dpRetDuc.dp_nominal':539} | {'dpRetDuc.dp_nominal':490*1.1}
48 | AirDucFou_20 | Air loop duct fouling - FIR=20% | {'dpRetDuc.dp_nominal':588} | {'dpRetDuc.dp_nominal':490*1.2}
49 | CHWPipFou_10 | Chilled water pipe fouling - FIR=10% | {'resCHW.dp_nominal':153670} | {'resCHW.dp_nominal':139700*1.1}
50 | CHWPipFou_20 | Chilled water pipe fouling - FIR=20% | {'resCHW.dp_nominal':167640} | {'resCHW.dp_nominal':139700*1.2}
51 | CHWPipIso_l02L25 | Chilled water pipe isolation - 20mm | {'resCHW.length':25} {'resCHW.thicknessIns':0.02}
52 | CHWPipIso_l005L25 | Chilled water pipe isolation - 5mm | {'resCHW.length':25} {'resCHW.thicknessIns':0.005}
53 | CooTowValLea_001 | Cooling tower valve leakage - leakage ratio l=0.001 | {'val.l':0.001}
54 | CooTowValLea_01 | Cooling tower valve leakage - leakage ratio l=0.01 | {'val.l':0.01}
55 | ChiConValLea_001 | Cooling water isolation valve leakage - leakage ratio l=0.001 | {'chiWSE.lValChi':[0.001,0.0001]}
56 | ChiConValLea_01 | Cooling water isolation valve leakage - leakage ratio l=0.01 | {'chiWSE.lValChi':[0.01,0.0001]}
57 | ChiEvaValLea_001 | Chilled water isolation valve leakage - leakage ratio l=0.001 | {'chiWSE.lValChi':[0.0001,0.001]}
58 | ChiEvaValLea_01 | Chilled water isolation valve leakage - leakage ratio l=0.01 | {'chiWSE.lValChi':[0.0001,0.01]}
59 | CooCoiValLea_001 | Cooling coil valve leakage - leakage ratio l=0.001 | {'watVal.l':0.001}
60 | CooCoiValLea_01 | Cooling coil valve leakage - leakage ratio l=0.01 | {'watVal.l':0.01}
61 | CooCoiValStuck_0 | Cooling coil valve stuck - Position =0 | {'faultCoiVavStu.active':True} {'watVal.yStu':0}
62 | CooCoiValStuck_5 | Cooling coil valve stuck - Position =5% | {'faultCoiVavStu.active':True} {'watVal.yStu':0.05}
63 | CooCoiValStuck_15 | Cooling coil valve stuck - Position =15% | {'faultCoiVavStu.active':True} {'watVal.yStu':0.15}
64 | CooCoiValStuck_65 | Cooling coil valve stuck - Position =65% | {'faultCoiVavStu.active':True} {'watVal.yStu':0.65}
65 | CooCoiValStuck_100 | Cooling coil valve stuck - Position =100% | {'faultCoiVavStu.active':True} {'watVal.yStu':1}
66 | OADamLea_001 | Outdoor air damper leakage - leakage ratio l=0.001 | {'eco.damOut.l':0.001}
67 | OADamLea_01 | Outdoor air damper leakage - leakage ratio l=0.01 | {'eco.damOut.l':0.01}
68 | OADamStuck_0 | Outdoor air damper stuck - Position =0 | {'faultOADamStu.active':True} {'eco.yStu':0}
69 | OADamStuck_5 | Outdoor air damper stuck - Position =5% | {'faultOADamStu.active':True} {'eco.yStu':0.05}
70 | OADamStuck_15 | Outdoor air damper stuck - Position =15% | {'faultOADamStu.active':True} {'eco.yStu':0.15}
71 | OADamStuck_65 | Outdoor air damper stuck - Position =65% | {'faultOADamStu.active':True} {'eco.yStu':0.65}
72 | OADamStuck_100 | Outdoor air damper stuck - Position =100% | {'faultOADamStu.active':True} {'eco.yStu':1}
73 | CooCoiFou_10 | Cooling coil fouling - FIR=10% | {'cooCoi.UA_nominal':0.9*10021}
74 | CooCoiFou_30 | Cooling coil fouling -FIR=30% | {'cooCoi.UA_nominal':0.7*10021}
75 | CooCoiFou_50 | Cooling coil fouling - FIR=50% | {'cooCoi.UA_nominal':0.5*10021}
76 | ChiConFou_20 | Chiller condener fouling - FIR=20% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.02031,0.03281]]} {'chiFauMod.perChiFau_c1456':[[-4.278,0.6404,0.05028,0]]} {'chiFauMod.fauIntRat':0.2}
77 | ChiConFou_40 | Chiller condener fouling - FIR=40% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.02031,0.03281]]} {'chiFauMod.perChiFau_c1456':[[-4.278,0.6404,0.05028,0]]} {'chiFauMod.fauIntRat':0.4}
78 | ChiNonCon_25 | Chiller non-condensable gas - FIR=25% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.1033,0.1616]]} {'chiFauMod.perChiFau_c1456':[[-18.86,0.3135,3.150,0.8737]]} {'chiFauMod.fauIntRat':0.025}
79 | ChiNonCon_50 | Chiller non-condensable gas - FIR=50% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.1033,0.1616]]} {'chiFauMod.perChiFau_c1456':[[-18.86,0.3135,3.150,0.8737]]} {'chiFauMod.fauIntRat':0.05}
80 | ChiOveCha_20 | Chiller overcharging - FIR=20% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.01228,0.04126]]} {'chiFauMod.perChiFau_c1456':[[-8.854,0.2838,0.1807,0]]} {'chiFauMod.fauIntRat':0.2}
81 | ChiOveCha_40 | Chiller overcharging - FIR=40% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.01228,0.04126]]} {'chiFauMod.perChiFau_c1456':[[-8.854,0.2838,0.1807,0]]} {'chiFauMod.fauIntRat':0.4}
82 | ChiExcOil_30 | Chiller excess oil - FIR=30% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.008258,0.02976]]} {'chiFauMod.perChiFau_c1456':[[-6.513,0.007701,0,0.04893]]} {'chiFauMod.fauIntRat':0.3}
83 | ChiExcOil_60 | Chiller excess oil - FIR=60% | {'chiFauMod.active':True} {'chiFauMod.perChiFau_c23':[[-0.008258,0.02976]]} {'chiFauMod.perChiFau_c1456':[[-6.513,0.007701,0,0.04893]]} {'chiFauMod.fauIntRat':0.6}
84 | pumChiCaviation | Chilled water pump caviation | {'pumChiPreArr':[1.21,1.02,0.66,0.44]} {'pumChietaArr':[0.51]} | [1.5,1.3,1.0,0.6]
85 | pumChiImpeller | Chilled water pump impeller fault | {'pumChiPreArr':[1.13,0.89,0.54,0.25]} {'pumChietaArr':[0.48]}
86 | pumChiMotDeg_15 | Chilled water pump motor degradation - 15% | {'pumChietaArr':[0.595]}
87 | pumChiMotDeg_30 | Chilled water pump motor degradation - 30% | {'pumChietaArr':[0.49]}
88 | pumCWCaviation | Cooling water pump caviation | {'pumCWPreArr':[0.97,0.86,0.66,0.44]} {'pumCWetaArr':[0.51]} | [1.2,1.1,1.0,0.6]
89 | pumCWImpeller | Cooling water pump impeller fault | {'pumCWPreArr':[0.9,0.75,0.54,0.25]} {'pumCWetaArr':[0.48]}
90 | pumCWMotDeg_15 | Cooling water pump motor degradation - 15% | {'pumCWetaArr':[0.595]}
91 | pumCWMotDeg_30 | Cooling water pump motor degradation - 30% | {'pumCWetaArr':[0.49]}
92 | fanAHUMotDeg_15 | Fan motor degradation - 15% | {'fanSup.per.motorEfficiency.eta':[0.595]}
93 | fanAHUMotDeg_30 | Fan motor degradation - 30% | {'fanSup.per.motorEfficiency.eta':[0.49]}
94 | cooTowFou_10 | Cooling tower fouling - FIR=10% | {'cooTow.per.UA_nominal':0.9*34115}
95 | cooTowFou_30 | Cooling tower fouling - FIR=30% | {'cooTow.per.UA_nominal':0.7*34115}
96 | cooTowFou_50 | Cooling tower fouling - FIR=50% | {'cooTow.per.UA_nominal':0.5*34115}
97 | conkTSup_5 | Supply air temperature PID loop fault - P=5 | {'conAHU.kTSup':5}
98 | conkTSup_05 | Supply air temperature PID loop fault - P=0.05 | {'conAHU.kTSup':0.05}
99 | conkFanSpe_10 | Supply fan speed PID loop fault - P=10 | {'conAHU.kFanSpe':10}
100 | conkFanSpe_01 | Supply fan speed PID loop fault - P=0.01 | {'conAHU.kFanSpe':0.01}
101 | conkMinOut_5 | Economizer PID loop fault - P=0.5 | {'conAHU.kMinOut':0.5}
102 | conkMinOut_005 | Economizer PID loop fault - P=0.005 | {'conAHU.kMinOut':0.005}
103 | conkPumSpe_1 | Chilled water pump speed PID loop fault - P=1 | {'pumSpe.k':1}
104 | conkPumSpe_01 | Chilled water pump speed PID loop fault - P=0.01 | {'pumSpe.k':0.01}
105 | conkCooTow_1 | Cooling tower speed PID loop fault - P=1 | {'cooTowSpeCon.conPID.k':1}
106 | conkCooTow_01 | Cooling tower speed PID loop fault - P=0.01 | {'cooTowSpeCon.conPID.k':0.01}
107 | conVAVSoukCoo_1 | South zone air cooling PID loop fault - P=1 | {'conVAVSou.kCoo':1}
108 | conVAVSoukCoo_01 | South zone air cooling PID loop fault - P=0.01 | {'conVAVSou.kCoo':0.01}
109 | conVAVSoukDam_5 | South zone VAV damper PID loop fault - P=5 | {'conVAVSou.kDam':5}
110 | conVAVSoukDam_05 | South zone VAV damper PID loop fault - P=0.05 | {'conVAVSou.kDam':0.05}
111 | maxCHWDifPreSP | Chilled water differential pressure setpoint falsely set to the maximum | {'faultCHWDifPre.active':True}
112 | maxCHWTSupSP | Chilled water supply temperature setpoint falsely set to the maximum | {'faultCHWTSupSet.active':True}
113 | yCooDel_1 | Cooling coil control signal delay - 1s | {'faultyCooDel.active':True}
114 | supFanSpeDel_1 | Supply fan speed control signal delay - 1s | {'faultSupFanSpeDel.active':True}
115 | yPumDel_1 | Chilled water pump speed control signal delay - 1s | {'faultyPumDel.active':True}
116 | infiltration_70 | More infiltration - dp_nominal_FIR=70% | {'flo.leaEas.res.dp_nominal':35} {'flo.leaSou.res.dp_nominal':35} {'flo.leaWes.res.dp_nominal':35} {'flo.leaNor.res.dp_nominal':35}
117 | infiltration_50 | More infiltration - dp_nominal_FIR=50% | {'flo.leaEas.res.dp_nominal':25} {'flo.leaSou.res.dp_nominal':25} {'flo.leaWes.res.dp_nominal':25} {'flo.leaNor.res.dp_nominal':25}
118 | schedule_early_1 | Schedule fault - Early termination of setback for 1 hour | {'occSch.occupancy':[18000,68400]}
119 | schedule_early_2 | Schedule fault - Early termination of setback for 2 hours | {'occSch.occupancy':[14400,68400]}
120 | schedule_delay_1 | Schedule fault - Delayed onset of setback for 1 hours | {'occSch.occupancy':[21600,72000]}
121 | schedule_delay_2 | Schedule fault - Delayed onset of setback for 2 hours | {'occSch.occupancy':[21600,75600]}
122 | schedule_nosetback | Schedule fault - No temperature setback | {'TZonSet.TZonCooOff':297.15}
123 | AHUFan_oversized | Oversized AHU supply fan | {'fanSup.per.pressure.V_flow':[1.4,4.2,7,8.4]} {'fanSup.per.pressure.dp':[1860,1750,1530,930]}
124 | AHUCooCoil_oversized | Oversized AHU cooling coil | {'cooCoi.m1_flow_nominal':5.1} {'cooCoi.m2_flow_nominal':8.4} {'cooCoi.UA_nominal':12895} {'cooCoi.dp1_nominal':48000} {'pumChiPreArr':[1.65,1.43,1.1,0.66]} | {'cooCoi.m1_flow_nominal':3.996} {'cooCoi.m2_flow_nominal':6.714} {'cooCoi.UA_nominal':10021} {'cooCoi.dp1_nominal':30000}
125 | CHWPump_oversized | Oversized chilled water pump | {'pumChiVFloArr':[0.25,0.75,1.25,1.5]} {'pumChiPreArr':[2.1,1.8,1.4,0.9]}
126 | CWPump_oversized | Oversized cooling water pump | {'pumCWVFloArr':[0.25,0.75,1.25,1.5]} {'pumCWPreArr':[1.7,1.6,1.4,0.87]}
127 | Chiller_oversized | Oversized chiller | {'QEva_nominal':-126000}