## CoolingSeason
index | scenarios |  | faultparameters
0 | BaselineSystem |  | {'THWSup.bias.k':0}
1 | THWSup_p2 | Hot water supply temperature sensor positive bias - 2 K | {'faultTHWSup.active':True} {'THWSup.bias.k':2}
2 | THWSup_m2 | Hot water supply temperature sensor negative bias - 4 K | {'faultTHWSup.active':True} {'THWSup.bias.k':-2}
3 | THWSup_p4 | Hot water supply temperature sensor positive bias - 2 K | {'faultTHWSup.active':True} {'THWSup.bias.k':4}
4 | THWSup_m4 | Hot water supply temperature sensor negative bias - 4K | {'faultTHWSup.active':True} {'THWSup.bias.k':-4}
5 | RelPreHW_p5000 | Hot water differential pressure sensor positive bias - 5000 Pa | {'faultRelPreHW.active':True} {'senRelPreHW.bias.k':5000}
6 | RelPreHW_m5000 | Hot water differential pressure sensor negative bias - 5000 Pa | {'faultRelPreHW.active':True} {'senRelPreHW.bias.k':-5000}
7 | RelPreHW_p10000 | Hot water differential pressure sensor positive bias - 10000 Pa | {'faultRelPreHW.active':True} {'senRelPreHW.bias.k':10000}
8 | RelPreHW_m10000 | Hot water differential pressure sensor negative bias - 10000 Pa | {'faultRelPreHW.active':True} {'senRelPreHW.bias.k':-10000}
9 | Vout_p15 | Outdoor air flow rate sensor positive scale error - 15% | {'faultVOut.active':True} {'VOut1.sca.k':1.15}
10 | Vout_m15 | Outdoor air flow rate sensor negative scale error - 15% | {'faultVOut.active':True} {'VOut1.sca.k':0.85}
11 | Vout_p30 | Outdoor air flow rate sensor positive scale error - 30% | {'faultVOut.active':True} {'VOut1.sca.k':1.3}
12 | Vout_m30 | Outdoor air flow rate sensor negative scale error - 30% | {'faultVOut.active':True} {'VOut1.sca.k':0.7}
13 | TSup_p1 | AHU supply air temperature sensor positive bias - 1 K | {'faultTSup.active':True} {'TSup.bias.k':1}
14 | TSup_m1 | AHU supply air temperature sensor negative bias - 1 K | {'faultTSup.active':True} {'TSup.bias.k':-1}
15 | TSup_p2 | AHU supply air temperature sensor positive bias - 2 K | {'faultTSup.active':True} {'TSup.bias.k':2}
16 | TSup_m2 | AHU supply air temperature sensor negative bias - 2K | {'faultTSup.active':True} {'TSup.bias.k':-2}
17 | TMix_p1 | Mix air temperature sensor positive bias - 1 K | {'faultTMix.active':True} {'TMix.bias.k':1}
18 | TMix_m1 | Mix air temperature sensor negative bias - 1 K | {'faultTMix.active':True} {'TMix.bias.k':-1}
19 | TMix_p2 | Mix air temperature sensor positive bias - 2 K | {'faultTMix.active':True} {'TMix.bias.k':2}
20 | TMix_m2 | Mix air temperature sensor negative bias - 2K | {'faultTMix.active':True} {'TMix.bias.k':-2}
21 | TRet_p1 | Return air temperature sensor positive bias - 1 K | {'faultTRet.active':True} {'TRet.bias.k':1}
22 | TRet_m1 | Return air temperature sensor negative bias - 1 K | {'faultTRet.active':True} {'TRet.bias.k':-1}
23 | TRet_p2 | Return air temperature sensor positive bias - 2 K | {'faultTRet.active':True} {'TRet.bias.k':2}
24 | TRet_m2 | Return air temperature sensor negative bias - 2K | {'faultTRet.active':True} {'TRet.bias.k':-2}
25 | RelPreAir_p15 | Air loop differential pressure sensor positive bias - 15 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':15}
26 | RelPreAir_m15 | Air loop differential pressure sensor negative bias - 15 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':-15}
27 | RelPreAir_p25 | Air loop differential pressure sensor positive bias - 25 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':25}
28 | RelPreAir_m25 | Air loop differential pressure sensor negative bias - 25 Pa | {'faultdpDisSupFan.active':True} {'dpDisSupFan.bias.k':-25}
29 | TAirEas_p1 | East zone air temperature sensor positive bias - 1K | {'faulttemAirEas.active':True} {'flo.temAirEas.bias.k':1}
30 | TAirEas_m1 | East zone air temperature sensor negative bias - 1K | {'faulttemAirEas.active':True} {'flo.temAirEas.bias.k':-1}
31 | TAirEas_p2 | East zone air temperature sensor positive bias - 2K | {'faulttemAirEas.active':True} {'flo.temAirEas.bias.k':2}
32 | TAirEas_m2 | East zone air temperature sensor negative bias - 2K | {'faulttemAirEas.active':True} {'flo.temAirEas.bias.k':-2}
33 | TSupEas_p1 | East zone discharging air temperature sensor positive bias - 1K | {'faultTSupEas.active':True} {'TSupEas.bias.k':1}
34 | TSupEas_m1 | East zone discharging air temperature sensor negative bias - 1K | {'faultTSupEas.active':True} {'TSupEas.bias.k':-1}
35 | TSupEas_p2 | East zone discharging air temperature sensor positive bias - 2K | {'faultTSupEas.active':True} {'TSupEas.bias.k':2}
36 | TSupEas_m2 | East zone discharging air temperature sensor negative bias - 2K | {'faultTSupEas.active':True} {'TSupEas.bias.k':-2}
37 | VSupEas_flow_p15 | East zone air flow rate sensor positive scale error - 15% | {'faultVSupEas_flow.active':True} {'VSupEas_flow.sca.k':1.15}
38 | VSupEas_flow_m15 | East zone air flow rate sensor negative scale error - 15% | {'faultVSupEas_flow.active':True} {'VSupEas_flow.sca.k':0.85}
39 | VSupEas_flow_p30 | East zone air flow rate sensor positive scale error - 30% | {'faultVSupEas_flow.active':True} {'VSupEas_flow.sca.k':1.3}
40 | VSupEas_flow_m30 | East zone air flow rate sensor negative scale error - 30% | {'faultVSupEas_flow.active':True} {'VSupEas_flow.sca.k':0.7}
41 | SupDucLea_10 | Air loop supply duct leakage - FIR=10% | {'faultSupDucLea.active':True} {'leaFra.k':-0.12} | {'faultSupDucLea.active':True} {'leaFra.k':-0.1*1.2}
42 | SupDucLea_20 | Air loop supply duct leakage - FIR=20% | {'faultSupDucLea.active':True} {'leaFra.k':-0.24} | {'faultSupDucLea.active':True} {'leaFra.k':-0.2*1.2}
43 | AirDucFou_10 | Air loop duct fouling - FIR=10% | {'dpRetDuc.dp_nominal':539} | {'dpRetDuc.dp_nominal':490*1.1}
44 | AirDucFou_20 | Air loop duct fouling - FIR=20% | {'dpRetDuc.dp_nominal':588} | {'dpRetDuc.dp_nominal':490*1.2}
45 | HWPipFou_10 | Hot water pipe fouling - FIR=10% | {'resHW.dp_nominal':93500} | {'resHW.dp_nominal':85000*1.1}
46 | HWPipFou_20 | Hot water pipe fouling - FIR=20% | {'resHW.dp_nominal':102000} | {'resHW.dp_nominal':85000*1.2}
47 | HWPipIso_l02L25 | Hot water pipe isolation - 20mm | {'resHW.length':25} {'resHW.thicknessIns':0.02}
48 | HWPipIso_l005L25 | Hot water pipe isolation - 5mm | {'resHW.length':25} {'resHW.thicknessIns':0.005}
49 | boiValLea_001 | Boiler isolation valve leakage - leakage ratio l=0.001 | {'boiIsoVal.l':0.001}
50 | boiValLea_01 | Boiler isolation valve leakage - leakage ratio l=0.01 | {'boiIsoVal.l':0.01}
51 | boiBypValLea_001 | Boiler bypass valve leakage - leakage ratio l=0.001 | {'valBypBoi.l':0.001}
52 | boiBypValLea_01 | Boiler bypass valve leakage - leakage ratio l=0.01 | {'valBypBoi.l':0.01}
53 | HeaCoiValLea_001 | Heating coil valve leakage - leakage ratio l=0.001 | {'HWVal.l':0.001}
54 | HeaCoiValLea_01 | Heating coil valve leakage - leakage ratio l=0.01 | {'HWVal.l':0.01}
55 | HeaCoiValStuck_0 | Heating coil valve stuck - Position =0 | {'faultHeaVavStu.active':True} {'HWVal.yStu':0}
56 | HeaCoiValStuck_5 | Heating coil valve stuck - Position =5% | {'faultHeaVavStu.active':True} {'HWVal.yStu':0.05}
57 | HeaCoiValStuck_15 | Heating coil valve stuck - Position =15% | {'faultHeaVavStu.active':True} {'HWVal.yStu':0.15}
58 | HeaCoiValStuck_65 | Heating coil valve stuck - Position =65% | {'faultHeaVavStu.active':True} {'HWVal.yStu':0.65}
59 | HeaCoiValStuck_100 | Heating coil valve stuck - Position =100% | {'faultHeaVavStu.active':True} {'HWVal.yStu':1}
60 | OADamLea_001 | Outdoor air damper leakage - leakage ratio l=0.001 | {'eco.damOut.l':0.001}
61 | OADamLea_01 | Outdoor air damper leakage - leakage ratio l=0.01 | {'eco.damOut.l':0.01}
62 | OADamStuck_0 | Outdoor air damper stuck - Position =0 | {'faultOADamStu.active':True} {'eco.yStu':0}
63 | OADamStuck_5 | Outdoor air damper stuck - Position =5% | {'faultOADamStu.active':True} {'eco.yStu':0.05}
64 | OADamStuck_15 | Outdoor air damper stuck - Position =15% | {'faultOADamStu.active':True} {'eco.yStu':0.15}
65 | OADamStuck_65 | Outdoor air damper stuck - Position =65% | {'faultOADamStu.active':True} {'eco.yStu':0.65}
66 | OADamStuck_100 | Outdoor air damper stuck - Position =100% | {'faultOADamStu.active':True} {'eco.yStu':1}
67 | HeaCoiFou_10 | Heating coil fouling - FIR=10% | {'heaCoi.UA_nominal_FIR':0.9} | {'heaCoi.UA_nominal':0.9*1399.21}
68 | HeaCoiFou_30 | Heating coil fouling -FIR=30% | {'heaCoi.UA_nominal_FIR':0.7} | {'heaCoi.UA_nominal':0.7*1399.21}
69 | HeaCoiFou_50 | Heating coil fouling - FIR=50% | {'heaCoi.UA_nominal_FIR':0.5} | {'heaCoi.UA_nominal':0.5*1399.21}
70 | boiFou_10 | Boiler fouling - FIR=20% | {'boi.eta_fou':0.81} |  | Practically every fuel leaves a certain amount of deposit on the fireside of the tubes. This is called fouling, and it reduces heat transfer dramatically. Tests show that a soot layer just 0.8 mm (0.03 in.) thick reduces heat transfer by 9.5 percent and a 4.5 mm (0.18 in.) layer by 69 percent. Deposits (called scale) on the waterside of the boiler tubes can impair heat transfer. They can also reduce boiler efficiency, restrict water circulation and lead to serious mechanical and operating problems. Scale causes the tubes metal temperature to rise, which increases the flue gas temperature. In extreme cases, the tubes fail from overheating. One millimetre of scale build-up can increase fule consumption by two percent.
71 | boiFou_20 | Boiler fouling - FIR=40% | {'boi.eta_fou':0.72} |  | https://www.etcc-ca.com/sites/default/files/OLD/images/boiler_research_project_-_ats-te_final_report_pcb_05092012.pdf
72 | pumHWCavitation | Hot water pump caviation | {'pumHWPreArr':[1.21,1.02,0.66,0.44]} {'pumHWetaArr':[0.51]} | [1.5,1.3,1.0,0.6] | https://www.cibsejournal.com/cpd/modules/2019-07-gas/ https://www.researchgate.net/figure/ariation-of-condensing-boiler-efficiency-with-the-load-and-the-return-temperature_fig3_276926502
73 | pumHWImpeller | Hot water pump impeller fault | {'pumHWPreArr':[1.13,0.89,0.54,0.25]} {'pumHWetaArr':[0.48]}
74 | pumHWMotDeg_15 | Hot water pump motor degradation - 15% | {'pumHWetaArr':[0.595]}
75 | pumHWMotDeg_30 | Hot water pump motor degradation - 30% | {'pumHWetaArr':[0.49]}
76 | fanAHUMotDeg_15 | Fan motor degradation - 15% | {'fanSup.per.motorEfficiency.eta':[0.595]}
77 | fanAHUMotDeg_30 | Fan motor degradation - 30% | {'fanSup.per.motorEfficiency.eta':[0.49]}
78 | conkTSup_1 | Supply air temperature PID loop fault - P=1 | {'conAHU.kTSup':1}
79 | conkTSup_01 | Supply air temperature PID loop fault - P=0.01 | {'conAHU.kTSup':0.01}
80 | conkFanSpe_10 | Supply fan speed PID loop fault - P=10 | {'conAHU.kFanSpe':10}
81 | conkFanSpe_01 | Supply fan speed PID loop fault - P=0.01 | {'conAHU.kFanSpe':0.01}
82 | conkMinOut_1 | Economizer PID loop fault - P=0.1 | {'conAHU.kMinOut':0.1}
83 | conkMinOut_001 | Economizer PID loop fault - P=0.001 | {'conAHU.kMinOut':0.001}
84 | conkPumHWSpe_5 | Hot water pump speed PID loop fault - P=5 | {'pumSpeHW.k':5}
85 | conkPumHWSpe_05 | Hot water pump speed PID loop fault - P=0.05 | {'pumSpeHW.k':0.05}
86 | conVAVEaskCoo_1 | East zone air cooling PID loop fault - P=1 | {'conVAVEas.kCoo':1}
87 | conVAVEaskCoo_01 | East zone air cooling PID loop fault - P=0.01 | {'conVAVEas.kCoo':0.01}
88 | conVAVEaskDam_5 | East zone VAV damper PID loop fault - P=5 | {'conVAVEas.kDam':5}
89 | conVAVEaskDam_05 | East zone VAV damper PID loop fault - P=0.05 | {'conVAVEas.kDam':0.05}
90 | maxHWDifPreSP | Hot water differential pressure setpoint falsely set to the maximum | {'faultHWDifPre.active':True}
91 | minHWTSupSP | Hot water supply temperature setpoint falsely set to the minimum | {'faultHWTSupSet.active':True}
92 | yHeaDel_1 | Heating coil control signal delay - 1s | {'faultyHeaDel.active':True}
93 | supFanSpeDel_1 | Supply fan speed control signal delay - 1s | {'faultSupFanSpeDel.active':True}
94 | yPumHWDel_1 | Hot water pump speed control signal delay - 1s | {'faultyPumHWDel.active':True}
95 | infiltration_70 | More infiltration - dp_nominal_FIR=70% | {'flo.leaEas.res.dp_nominal':35} {'flo.leaSou.res.dp_nominal':35} {'flo.leaWes.res.dp_nominal':35} {'flo.leaNor.res.dp_nominal':35}
96 | infiltration_50 | More infiltration - dp_nominal_FIR=50% | {'flo.leaEas.res.dp_nominal':25} {'flo.leaSou.res.dp_nominal':25} {'flo.leaWes.res.dp_nominal':25} {'flo.leaNor.res.dp_nominal':25}
97 | schedule_early_1 | Schedule fault - Early termination of setback for 1 hour | {'occSch.occupancy':[18000,68400]}
98 | schedule_early_2 | Schedule fault - Early termination of setback for 2 hours | {'occSch.occupancy':[14400,68400]}
99 | schedule_delay_1 | Schedule fault - Delayed onset of setback for 1 hours | {'occSch.occupancy':[21600,72000]}
100 | schedule_delay_2 | Schedule fault - Delayed onset of setback for 2 hours | {'occSch.occupancy':[21600,75600]}
101 | schedule_nosetback | Schedule fault - No temperature setback | {'TZonSet.TZonHeaOff':293.15}
102 | AHUFan_oversized | Oversized AHU supply fan | {'fanSup.per.pressure.V_flow':[1.4,4.2,7,8.4]} {'fanSup.per.pressure.dp':[1860,1750,1530,930]}
103 | AHUHeaCoil_oversized | Oversized AHU heating coil | {'heaCoi.m1_flow_nominal':2.5} {'heaCoi.m2_flow_nominal':5.0} {'heaCoi.UA_nominal_FIR':1.29} {'heaCoi.dp1_nominal':48000} {'pumHWPreArr':[1.65,1.43,1.1,0.66]} | {'heaCoi.m1_flow_nominal':1.93} {'heaCoi.m2_flow_nominal':4.03} {'heaCoi.UA_nominal':1399.21} {'heaCoi.dp1_nominal':30000} | 1.27 1.25 1.29 1.27 http://daikinapplied.co.id/wp-content/uploads/2012/10/CATALOGUE-AIR-HANDLING-UNIT-DDM-AHU.pdf
104 | HWPump_oversized | Oversized hot water pump | {'pumHWVFloArr':[0.25,0.75,1.25,1.5]} {'pumHWPreArr':[2.1,1.8,1.4,0.9]}
105 | Boiler_oversized | Oversized boiler | {'boi.Q_flow_nominal':50658} | 40526